## Sheet1
Object Type | Object Name | Instance | Units | Values
Analog Inputs (AI) | Room Temperature | AI:0 | 1/10 degrees Fahrenheit
Analog Inputs (AI) | Humidity | AI:1 | 1/10 %
Analog Inputs (AI) | CO2 | AI:2 | ppm
Analog Inputs (AI) | Pressure | AI:3 | PSI | -500 - 500
Analog Inputs (AI) | Universal Input 5 | AI:4
Analog Inputs (AI) | Ext Sensor Bus Temperature 1 | AI:5
Analog Inputs (AI) | Ext Sensor Bus Temperature 2 | AI:6
Analog Inputs (AI) | Ext Sensor Bus Temperature 3 | AI:7
Analog Inputs (AI) | Ext Sensor Bus Temperature 4 | AI:8
Analog Inputs (AI) | Ext Sensor Bus Humidity 1 | AI:9
Analog Inputs (AI) | Ext Sensor Bus Humidity 2 | AI:10
Analog Inputs (AI) | Ext Sensor Bus Humidity 3 | AI:11
Analog Inputs (AI) | Ext Sensor Bus Humidity 4 | AI:12
Analog Inputs (AI) | Ext Sensor Bus CO2 1 | AI:13
Analog Inputs (AI) | Ext Sensor Bus CO2 2 | AI:14
Analog Inputs (AI) | Ext Sensor Bus CO2 3 | AI:15
Analog Inputs (AI) | Ext Sensor Bus CO2 4 | AI:16
Analog Inputs (AI) | Ext Sensor Bus Pressure 1 | AI:17
Analog Inputs (AI) | Ext Sensor Bus Pressure 2 | AI:18
Analog Inputs (AI) | Ext Sensor Bus Pressure 3 | AI:19
Analog Inputs (AI) | Ext Sensor Bus Pressure 4 | AI:20
Binary Inputs (BI) | Occupancy Status | BI:0
Binary Inputs (BI) | Relay 1 | BI:1 |  | 0 = Off 1 = On
Binary Inputs (BI) | Relay 2 | BI:2 |  | 0 = Off 1 = On
Binary Inputs (BI) | Relay 3 | BI:3 |  | 0 = Off 1 = On
Binary Inputs (BI) | Relay 4 | BI:4 |  | 0 = Off 1 = On
Binary Inputs (BI) | Occupancy Status | BI:5
Binary Inputs (BI) | Ext Sensor Bus Occupancy 1 | BI:6
Binary Inputs (BI) | Ext Sensor Bus Occupancy 2 | BI:7
Binary Inputs (BI) | Ext Sensor Bus Occupancy 3 | BI:8
Binary Inputs (BI) | Ext Sensor Bus Occupancy 4 | BI:9
Binary Values (BV) | Relay 1 Enable | BV:0 |  | 0 = Disabled 1 = Enabled
Binary Values (BV) | Relay 2 Enable | BV:1 |  | 0 = Disabled 1 = Enabled
Binary Values (BV) | Relay 3 Enable | BV:2 |  | 0 = Disabled 1 = Enabled
Binary Values (BV) | Relay 4 Enable | BV:3 |  | 0 = Disabled 1 = Enabled
Binary Values (BV) | Relay 5 Enable | BV:4 |  | 0 = Disabled 1 = Enabled
Binary Values (BV) | Analog Out 1 Enable | BV:5 |  | 0 = Disabled 1 = Enabled
Binary Values (BV) | Analog Out 2 Enable | BV:6 |  | 0 = Disabled 1 = Enabled
Binary Values (BV) | Analog Out 1 Pulse Enable | BV:7
Binary Values (BV) | Analog Out 2 Pulse Enable | BV:8
Binary Values (BV) | Enable Force Occupied | BV:9 |  | 0 = Disabled 1 = Enabled
Binary Values (BV) | Enable Auto Away | BV:10 |  | 0 = Disabled 1 = Enabled
Binary Values (BV) | Unoccupied Mode | BV:11 |  | 0 = Occupied 1 = Unoccupied
Binary Values (BV) | Show Centigrade | BV:12 |  | 0 = Disabled 1 = Enabled
Binary Values (BV) | Enable Onboard Temp/Humi Sensor | BV:13
Binary Values (BV) | Enable Onboard CO2/Occu Sensors | BV:14
Binary Values (BV) | Display Desired Temp | BV:15
Binary Values (BV) | Reboot the Device | BV:16
Multi-state Inputs (MI) | Operating Mode | MI:0 |  | 0 = OFF 1 = HEATING 2 = COOLING
Multi-state Inputs (MI) | Active Conditioning Mode | MI:1 |  | 0 = OFF 1 = AUTO 2 = HEATING 3 = COOLING
Multi-state Inputs (MI) | Active Fan Speed | MI:2 |  | 0 = OFF 1 = AUTO 2 = LOW 3 = MEDIUM 4 = HIGH
Multi-state Inputs (MI) | Occupancy State | MI:3
Analog Values (AV) | Set Temperature Heating | AV:0 | 2 x Fahrenheit | 120-180 (60.0 - 90.0)
Analog Values (AV) | Set Temperature Cooling | AV:1 | 2 x Fahrenheit | 120-180 (60.0 - 90.0)
Analog Values (AV) | Max Set Temperature Heating | AV:2
Analog Values (AV) | Min Set Temperature Heating | AV:3
Analog Values (AV) | Max Set Temperature Cooling | AV:4
Analog Values (AV) | Min Set Temperature Cooling | AV:5
Analog Values (AV) | Temperature Offset | AV:6 | 1/10 degrees Fahrenheit | -100 - 100 (-10.0 - 10.0)
Analog Values (AV) | Heating Deadband | AV:7 | 1/10 degrees Fahrenheit | 0-100 (0.0-10.0)
Analog Values (AV) | Cooling Deadband | AV:8 | 1/10 degrees Fahrenheit | 0-100 (0.0-10.0)
Analog Values (AV) | Min Humidity Setpoint | AV:9
Analog Values (AV) | Max Humidity Setpoint | AV:10
Analog Values (AV) | Analog Out 1 Min Setting | AV:11
Analog Values (AV) | Analog Out 2 Min Setting | AV:12
Analog Values (AV) | Analog Out 1 Max Setting | AV:13
Analog Values (AV) | Analog Out 2 Max Setting | AV:14
Analog Values (AV) | Zone CO2 Dampper Opening Rate | AV:15
Analog Values (AV) | Zone CO2 Threshold | AV:16 | ppm | 0-2000
Analog Values (AV) | Zone CO2 Target | AV:17 | ppm | 0-2000
Analog Values (AV) | Proportional Constant | AV:18 | 1/100 | 0-100
Analog Values (AV) | Integral Constant | AV:19 | 1/100 | 0-100
Analog Values (AV) | Proportional Temperature Range | AV:20 | 1/10 degrees Fahrenheit | 0-100 (0.0-10.0)
Analog Values (AV) | Integration Time | AV:21 | minutes | 5-100
Analog Values (AV) | Unoccupied Setback | AV:22 | 1/10 degrees Fahrenheit | 10-200 (1.0-20.0)
Analog Values (AV) | Heating Deadband Multiplier | AV:23
Analog Values (AV) | Relay Activation Hysteresis | AV:24 | % | 1-50
Analog Values (AV) | Analog Fan Speed Multiplier | AV:25 | 1/10 | 1-100 (0.1-10)
Analog Values (AV) | Humidity Hysteresis | AV:26 | % | 1-100
Analog Values (AV) | Forced Occupied Time | AV:27 | minutes | 0-255
Analog Values (AV) | Auto Away Time | AV:28 | minutes | 0-255
Analog Values (AV) | Auto Away Setback Temperature | AV:29
Analog Values (AV) | FCU Aux Heating 1 Activate | AV:30 | 1/10 Degrees Fahrenheit | 10-100 (1.0 - 10.0)
Analog Values (AV) | FCU Two-Pipe Heating Threshold | AV:31 | Degrees Fahrenheit | 70-130
Analog Values (AV) | FCU Two-Pipe Cooling Threshold | AV:32 | Degrees Fahrenheit | 35-70
Analog Values (AV) | FCU Water Valve Sampling On Time | AV:33 | minutes | 0-30
Analog Values (AV) | FCU Water Valve Sampling Wait Time | AV:34 | minutes | 5-255
Analog Values (AV) | FCU Water Valve Sampling During Loop Deadband On Time | AV:35 | minutes | 0-30
Analog Values (AV) | FCU Water Valve Sampling During Loop Deadband Wait Time | AV:36 | minutes | 5-255
Analog Values (AV) | Fail-Safe Time | AV:37 | minutes | 0-65535 where 0 means fail safe will be disable
Analog Values (AV) | Cooling Stage 1 Fan Output | AV:38 | 1/10 Volts | 0 - 100 (0.0 - 10.0)
Analog Values (AV) | Cooling Stage 2 Fan Output | AV:39 | 1/10 Volts | 0 - 100 (0.0 - 10.0)
Analog Values (AV) | Heating Stage 1 Fan Output | AV:40 | 1/10 Volts | 0 - 100 (0.0 - 10.0)
Analog Values (AV) | Heating Stage 2 Fan Output | AV:41 | 1/10 Volts | 0 - 100 (0.0 - 10.0)
Analog Values (AV) | Linear Fan Speed Level Low | AV:42
Analog Values (AV) | Linear Fan Speed Level High | AV:43
Analog Values (AV) | Staged Fan Speed Level Low | AV:44
Analog Values (AV) | Staged Fan Speed Level High | AV:45
Analog Values (AV) | Analog Out Fan Default | AV:46
Analog Values (AV) | Fan Runtime Post Conditioning | AV:47
Analog Values (AV) | Staged Fan Analog Out at Recirculation | AV:48
Analog Values (AV) | Installer Lock Pin | AV:49
Analog Values (AV) | User Lock Pin | AV:50
Analog Values (AV) | Stage Up Timer | AV:51
Analog Values (AV) | Stage Down Timer | AV:52
Multi-state Values (MV) | Conditioning Mode | MV:0 |  | 0 = OFF 1 = AUTO 2 = HEATING 3 = COOLING
Multi-state Values (MV) | Fan Speed | MV:1 |  | 0 = OFF 1 = AUTO 2 = LOW 3 = MEDIUM 4 = HIGH
Multi-state Values (MV) | Temperature Mode | MV:2 |  | 0 = Single Setpoint 1 = Dual Setpoint Fixed Deadband 2 = Dual Setpoint Variable Deadband
Multi-state Values (MV) | HVAC Profile | MV:3
Multi-state Values (MV) | Relay 1 Mapping | MV:4 |  | • None • Cooling Stage 1 • Cooling Stage 2 • Heating Stage 1 • Heating Stage 2 • Fan Low Speed • Fan High Speed • Fan Enable • Occupied Enable • Humidifier • Dehumidifier • Externally Mapped • DVC Damper • Compressor Stage 1 • Compressor Stage 2 • Aux Heating • O- Energize in Cooling • B- Energize in Heating • Water Valve • Fan Low Speed - Ventilation • Cooling Water Valve • Heating Water Valve
Multi-state Values (MV) | Relay 2 Mapping | MV:5 |  | • None • Cooling Stage 1 • Cooling Stage 2 • Heating Stage 1 • Heating Stage 2 • Fan Low Speed • Fan High Speed • Fan Enable • Occupied Enable • Humidifier • Dehumidifier • Externally Mapped • DVC Damper • Compressor Stage 1 • Compressor Stage 2 • Aux Heating • O- Energize in Cooling • B- Energize in Heating • Water Valve • Fan Low Speed - Ventilation • Cooling Water Valve • Heating Water Valve
Multi-state Values (MV) | Relay 3 Mapping | MV:6 |  | • None • Cooling Stage 1 • Cooling Stage 2 • Heating Stage 1 • Heating Stage 2 • Fan Low Speed • Fan High Speed • Fan Enable • Occupied Enable • Humidifier • Dehumidifier • Externally Mapped • DVC Damper • Compressor Stage 1 • Compressor Stage 2 • Aux Heating • O- Energize in Cooling • B- Energize in Heating • Water Valve • Fan Low Speed - Ventilation • Cooling Water Valve • Heating Water Valve
Multi-state Values (MV) | Relay 4 Mapping | MV:7 |  | • None • Cooling Stage 1 • Cooling Stage 2 • Heating Stage 1 • Heating Stage 2 • Fan Low Speed • Fan High Speed • Fan Enable • Occupied Enable • Humidifier • Dehumidifier • Externally Mapped • DVC Damper • Compressor Stage 1 • Compressor Stage 2 • Aux Heating • O- Energize in Cooling • B- Energize in Heating • Water Valve • Fan Low Speed - Ventilation • Cooling Water Valve • Heating Water Valve
Multi-state Values (MV) | Relay 5 Mapping | MV:8 |  | • None • Cooling Stage 1 • Cooling Stage 2 • Heating Stage 1 • Heating Stage 2 • Fan Low Speed • Fan High Speed • Fan Enable • Occupied Enable • Humidifier • Dehumidifier • Externally Mapped • DVC Damper • Compressor Stage 1 • Compressor Stage 2 • Aux Heating • O- Energize in Cooling • B- Energize in Heating • Water Valve • Fan Low Speed - Ventilation • Cooling Water Valve • Heating Water Valve
Multi-state Values (MV) | Analog Out 1 Mapping | MV:9 |  | • Cooling • Linear Fan Speed • Heating • Staged Fan Speed • Externally Mapped - Analog • DCV Modulating Damper • Compressor Speed • Fan Speed • Water Modulating Valve • Cooling Modulating Valve • Heating Modulating Valve
Multi-state Values (MV) | Analog Out 2 Mapping | MV:10 |  | • Cooling • Linear Fan Speed • Heating • Staged Fan Speed • Externally Mapped - Analog • DCV Modulating Damper • Compressor Speed • Fan Speed • Water Modulating Valve • Cooling Modulating Valve • Heating Modulating Valve
Multi-state Values (MV) | Universal In1 Mapping | MV:11 |  | • Discharge Air Temperature • Generic Alarm N/O • Generic Alarm N/C • Keycard Sensor (AI) • Door/Window Sensor N/C - Title24 • Door/Window Sensor (AI) • Fan Run Status N/O • Fan Run Status N/C • Door/Window Sensor N/O - Title24 • Door/Window Sensor N/C • Door/Window Sensor N/O • Keycard Sensor N/O • Keycard Sensor N/C • Chilled Water Supply Temperature • Hot Water Supply Temperature • Current TX (0-10Amps) • Current TX (0-20Amps) • Current TX (0-50Amps) • Voltage Input • Thermistor Input